AMD 02 dates to match (mark hit / miss / constrained)

| 30% to OR | 60% to OR | 90% to OR | IFC | Const. start | XFMR delivery | Const. complete | Comm. complete | ISD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 30 Oct 2026 | 28 May 2027 | 29 Oct 2027 | 10 Dec 2027 | 10 Jan 2028 | 31 Jul 2028 | 24 Nov 2028 | 15 Dec 2028 | 15 Dec 2028 |
| P6: *? | P6: *? | P6: *? | P6: *? | P6: *? | P6: *? | P6: *? | P6: *? | P6: *? |

Read the print in this order — table first, Gantt last

| 1. Header | Data date, WBS filter, print date. Ask: is this the whole job or one WBS? |
| --- | --- |
| 2. Milestones | Fill the strip above. Hit / miss / * constrained. |
| 3. Status vs today | Not Started or In Progress with finish ≤ data date = already late. |
| 4. Float | 0–2w = driving or constrained. 40w+ on land/reviews/procurement = missing logic until proven otherwise. |
| 5. Star (*) dates | Assume a constraint. Constrained ISD with 0.0w float does not prove the work fits. |
| 6. Pred / succ | Does the gate wait on the right things? FS = finish-to-start; SS/FF = overlap; long lag (FS 9w) often hides missing work. |
| 7. Gantt last | Look for overlap (commission vs install), gaps (civil → XFMR), and summary bars hiding deliveries. |

Eight checks — fail = a written comment, not a feeling

| # | Check | What “good” looks like | Hare-specific watch item | Pass | Fail / N/A |
| --- | --- | --- | --- | --- | --- |
| 1 | WBS complete | One file covers every Exhibit G WBS. | DCP .001, Comms .002, Hendricks .005, TAM .006, TIF .008 (0.8 mi / WO 115469484). |  |  |
| 2 | Milestones coded | ISD, IFC, FSR/Gate 4, XFMR on site, breakers/CS on site, land close, outage are zero-duration flags. | Do not accept a 13-week “Transformer Process” in place of 31 Jul 2028 on-site. |  |  |
| 3 | Reviews precede gates | OR review finish → disposition → Gate. AMD 02: 30% 3 wks, 60/90% 2 wks, IFC 1 wk. | PD4500 FSR on 6 Nov cannot precede PD4210 comment return on 20 Nov unless the gate is marked conditional. |  |  |
| 4 | Company equipment visible | On-site dates for Company-furnished XFMR, 4×23 kV breakers, 115 kV circuit switcher. | AMD 02 restated XFMR only. Breaker/CS still §12 15 Jun 2028 unless Supply Chain updates. Kill MP2280 “Pending.” |  |  |
| 5 | Constraints listed | Planner attaches a list: activity, constraint type, reason. Duplicate view with constraints removed. | 90%, IFC, construction start, ISD have shown *. Constrained 0.0w ISD hides true slip. |  |  |
| 6 | No hanging work | Every activity has a predecessor and successor (except start/end). No “Pending” IDs. | 30%/60% reviews with 47–87w float are not on the driving path — comment incorporation is missing. |  |  |
| 7 | Interfaces are activities | Land, AQ, W90 outage/shoo-fly, wind-farm DTT/ADSS, Hendricks cutover exist as dated work. | Siting at 0.2w on 14 Sep with 77w land float is not a relocated-site plan. 30% must use the new parcel, not the retired GPS. |  |  |
| 8 | Late-2028 stack | Construction complete → commissioning duration → ISD. Float on the last 90 days is real. | AMD 02 wants const. complete 24 Nov and ISD 15 Dec. A 3-day “release” after a 5 Dec finish does not earn ISD. |  |  |

Two paths to name out loud  ·  30-minute review closeout

| Path A — next gate (now → 30 Oct 2026) What must be true for a complete, frozen 30% package on the new 0.8-mi-east site: locked parcel/coords, constructability walk, one-line / M&R IFR in the set, QA/QC done. First activity that can miss 30 Oct: ____________________ | Path B — ISD (last 90 days of 2028) XFMR on site 31 Jul → set/dress/test → electrical/physical complete → commission → 15 Dec ISD. First activity that can move ISD: ____________________ Float on that activity: ______ |
| --- | --- |
| Close the meeting with Failed checks (write IDs) · constraint report committed · next data date · who owns XFMR/breaker/CS dates · land notice yes/no · FSR vs comment-return decision. | Do not accept the file if Only one WBS is printed as “full schedule,” Exhibit D 2-mile TIF is still in the model, ISD is * with no constraint list, or 30% is aimed at the retired GPS. |